## Sheet1
Revised 5/19/2016
# | Questions: | Answers
1 | Does this program include truck drivers (vac trucks, phosphate haulers, etc)? | Yes. Any mobile equipment (or appurtenances) that extends vertically and could breach the 10 foot “No-go zone” is included. Please reference the “Exceptions to Scope” section on page 3 of 23 in the current program.
2 | Where does the measurement start – bottom neutral line, bottom fiber optic line? | Currently posted signs indicate distance to the lowest energized line. CAUTION: There may be lines below the posted energized line height and proper clearance determinations will be required to be implemented as was the case prior to the signs.
3 | What is the policy when traveling parallel to a power line (hauling /traveling) | Please refer to the table on page 16 of 23 in the current policy under “Traveling Parallel to HVOL” for requirements related to certain circumstances.
4 | Are contractors required to purchase a measuring device to check line clearance? | Contractors are not required to purchase measuring devices. But, if a contractor will utilize the policy on a regular basis, the contractor may want to purchase the device in order to be efficient. Mosaic site personnel will have access to devices.
5 | Why doesn’t Mosaic post the power line voltage with the clearance sign and include distance to ground wire and first power line? | Mosaic is currently considering revisions to the requirement for signs to have them include:
· The distance to the lowest energized line
· The distance to the lowest line (clearance), and
· The voltage of the lowest energized line
6 | There needs to be a clear lock-out tag-out policy / procedure for locking out power lines. | We are currently working with the electrical group to determine the best procedures when a line has to be de-energized.
7 | Sites need to be consistent. | We are working to communicate a consistent message, including the answers to submitted questions, to both contractors and Mosaic employees with responsibilities regarding the Mobile Equipment High Voltage Overhead Line Procedure to help ensure implementation will be consistent.
8 | Who is responsible for identifying vehicle height and labeling on rental equipment? | The person responsible for renting the equipment is responsible for identifying the height of the equipment and assuring the labels are in place.
9 | Can the mid axle berms be used for the 30-10-10 markers, some of the BMPS are miles long? | When mid-axle height berms, required by MSHA regulations, are in place such that they divide a portion of the 30-10 horizontal circumference and block the vehicle from entering a portion of the Caution Zone and/or Permit Zone, the berms are considered a sufficient warning and cones are not necessary for that portion of the zones.
10 | Can pre-planning for down days be done and permits prepared in advance? | Only portions of the permit that do not require field verification (generally Section 1) can be pre-populated with the appropriate information. Field verified information must be filled out once the field verification is completed. Permit approval requires field verification unless a verbal verification is indicated on the permit as an option (i.e., Area Superintendent/Manager approval).
11 | What if there is an insulated line coming from a pole to a structure and that insulated line continues in a cable tray? Does the policy apply? For example, lifting a drum of hydraulic fluid up to a structure where we would be within 10 feet of the insulated line. | The program has no exemptions for insulated overhead lines, in this case a permit and spotter would be required.
12 | Ground rod driver rig. Although it lays down for transport, it tilts upward and stands 12 feet for use – but “does not extend vertically” as mentioned in scope. Scope indicates: “Equipment that does not extend vertically and does not breach the 10 foot “No-go zone”.” | This is out of scope.
13 | Is the actual policy available for distribution? We have been given the training material but not a copy of the policy. | Policy is being “tweaked” based upon questions, issues, etc. (for example, the power line height is being adjusted to 27 ft as we will not count the neutral line) and will be available on the contractor website when finalized/approved. Should be the week of 1/11/2016.
A copy of the original policy was supposed to be included in the back of the spiral notebook type document Crane Tech handed out as training material. It is also posted on Livelink with Phosphate Safety Policies
14 | Excavators crossing under HVOL – After some research, it have not been identified with CAT equipment any locking mechanism (we or the rental company) that can physically lock the boom of an excavator. The hydraulic pressure can be turned off but it disables all the hydraulics rendering the machine inoperable. Having said that, any large capacity excavator will have the potential to extend into the no-go zone while crossing under a HVOL. | If you take the example of one of my current projects: Mosaic had to pioneer a 2-3 mile access for us to a site location. The access crosses under HVOL’s nine times and runs parallel under the line for a distance. Transports cannot access the area so the equipment must be walked out. The excavators will have the booms knuckled in but have no way to secure the boom. Depending on the machine, (regular or long boom) the boom could have the capability of reaching above the HLOV in some locations.
Similar to another question recently. The definition of “Equipment Traveling” includes: “…and the boom or vertical extensions in appropriate position for travel.”
Crossing under – Empty AND HVOL is 24 ft high and clearly marked = Evaluate the risks prior to travel and along intended route. No spotter or permit required.
15 | If there are multiple crossing in one general area, i.e. two lines cross over road in close proximity or road zig zags under same line like on the Rt. 37 Side of Two Penny, will one permit cover the general area? | Yes, but should be included and documented in permit approval process so there are no assumptions. The permit is designed for a period of time and as long as the hazards at each crossing are evaluated as part of the permit – it will apply.
16 | Has there been any discussion about line sag as the temperature changes? | There will be some difference in height related to temperature, but should not be more than a few inches. If the line looks like it is sagging more than a normal amount we need to have the line re-measured. The measurements should be taken at the lowest point.
17 | What is required when a Maintenance Truck equipped with a boom is traveling under a high voltage overhead line? The boom as mounted on the truck could reach 28 feet, but is secured in a cradle for travel at the truck bed at roughly the height of the cab and well below a 10ft distance from any power line. | A The program defines “Equipment Traveling” as: ”Qualifying equipment is considered to be traveling if the equipment is moving from one location to another with or without a load and the boom or vertical extensions in appropriate position for travel.” (Your scenario meets this definition as the boom is in the appropriate position for travel.)
The program section regarding applying 30-10-10 Ft Rule when traveling, and crossing under HVOL, has a table that indicates:
o If equipment is empty or is carrying a load that protrudes no more than 4 feet on either side. (You indicate that the equipment is empty) And,
o HVOL is 24 (now 27) ft high and clearly marked and have required line clearance distance, (you indicated that the boom in the secured position for travel is roughly at cab height – well below any height near the 10 ft “No-Go” zone.) Then,
o Evaluate risks prior to travel and along intended route. No spotter or permit required.
18 | Same vehicles traveling on corridor roads along power lines. | The program has a similar table to be utilized when traveling parallel to HVOL that indicates:
o If equipment is empty or carrying a load that protrudes no more than 4 feet on either side, And,
o Equipment and load are inside 30 horizontal feet, but outside 10 horizontal feet to HVOL, Then,
· Evaluate risk prior to travel and along intended route. No spotter required.
· Make sure that ALL of the required tests are made to follow decision tree to verified. For example, if the line is not marked, get a measurement on the line.
Added 2/4/2016
19 | Are all overhead power lines subject to the requirements and 30-10-10 rule or only certain voltage? | High Voltage Overhead Line is defined as 1000 AC volts phase to phase.
20 | What is the best way to ensure contractors working on the site property comply to the requirements of the program? Site doesn't necessarily know who the contractor is, what they're doing, or who is responsible for them. May come along a job where it doesn't look like the program is being followed. | Planning meetings should be conducted with our contractors and the contractor’s Mosaic point of contact (supervisor, project manager, etc.) where expectations should be conveyed. We should know who is on our sites at all times, those that work remotely are required to call in to the guard and provide company name, employees and where they or working and when they are finished for the day. We should know who is on our site. It is an MSHA requirement.
21 | Which line is clearance measured from? | Minimum Clearance Distances are defined in regulations and change based on voltage. 50kv requires a 10 foot minimum clearance. As voltage increases, the clearance distance requirement increases. Clearance distances refer to the energized line. Other lines may be posted to indicate whether there's enough room to avoid contact however a minimum distance isn't mandated by regulation or Mosaic.
Added 2/9/2016
22 | Who is responsible for completing the permit? All other Mosaic permits are completed by Mosaic authorized employees | The Mobile Equipment High Voltage Overhead Line (HVOL) 30-10-10 Ft Rule Procedure indicates that: “The permit must be completed by the equipment operator and dedicated spotter.” in the first paragraph on the permit, and in the process flow diagram. The permit does, however, require a Mosaic approver to verify all precautions have been completed.
Added 3/11/2016
23 | Does a Mosaic representative physically need to be present to approve? | Yes the Mosaic representative must be present so that verification of precautions can be made prior to approval.
24 | What is the policy/process/procedure when a HVOL needs to be de-energized prior to work being done? | When lines need to be de-energized and locked out, they will be locked out by the electrical group (equipment owner) and (mobile) equipment operators, spotters, and anyone exposed to hazardous energy will place personal locks on the lockbox brought to them by the electrical group. (Approved by the electrical team and GMs at the February MBR)
25 | If an overhead line is insulated, does the program apply? | Insulated lines are covered by the MEHVOL policy as the insulation cannot be inspected for damage as it can for insulated lines on the ground. They must be considered as an energized line. Also, the definition of overhead lines in the program would exclude lines in cable trays or on the ground. It reads: “Aerial power lines above 1,000 volts AC phase-to-phase.”(emphasis added).
26 | Q: How will equipment operators, spotters and other affected employees verify the lock-out of the overhead lines? | A: Since the affected employees do not “work on” the bare conductors, the workers (or workgroup representative) will witness the lock-out and confirm air gaps (between blades on breaker for medium voltage or between pole-top switches for 25Kv/69Kv) and blue lock applied to controls with equipment owner. Those keys will be placed into a lock-box for LOTO by the affected group. The spotter is another layer of protection to assure no contact is made with the lines.
Added 5/19/2016
27 | In the procedure for issuing a MEHVOL permit: "Follow the steps below to apply the 30-10-10 foot rule if equipment/load is at or within 10 ft. from the nearest HVOL." When the permit indicates that the line must be de-energized prior to working near the line - Is a spotter required? | A spotter is not required if the line is fully de-energized, locked out, and verified together by mobile equipment operator and equipment (line) owner.
.